Anexo 01

|  | System Information |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | System Voltage |  |  | 22,900 |  |  | V |
|  | Upstream Overcurrent Breaker (device) |  |  | 117 |  |  | A |
|  | Short Circuit Current (Isc) |  |  | 7.6 |  |  | kA |
|  | Energy Storage (e.g. Capacitors) |  |  | 0.0 |  |  | kJ |
|  | Opening Time |  |  | 0.10 |  |  | Sec |
|  | Working Distance (From the arc source) |  |  | 910 (36 in) |  |  | (*) |
|  | Power - For Arc Flash prot. Boundaries |  |  | 4,640.5 |  |  | kVA (*) |
|  | (*) Fixed or Automatic Value |  |  |  |  |  |  |
|  | Incident Energy |  |  | 10.7 |  |  | cal/cm2 |

Análisis de seguridad eléctrica

(imagen PPE) Ej:

Frontera de protección de arco y choque eléctrico

Distancias para instalación de barricada durante verificación de Seven Steps y señalización perimetral

| According to NFPA70E: Table 130.4(E)(a) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 1.5 m |  | 1.8 m | 0.8 m |  |  |  |  |  |  |
|  |  |  |  |  | 3 m |  |  |  |  |  |  |  |
|  |  |  |  |  | ñ |  |  |  |  |  |  |  |
| Exposed Movable Conductor |  |  |  |  |  |  |  |  |  |  |  |  |

Etiqueta NFPA70E

Etiqueta para imprimir y colocar en el área de trabajo

|  |  |  |  | WARNING |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Arc Flash & Shock Hazard Appropriate PPE Required |  |  |  |  |  |
|  | ARC FLASH PROTECTION BOUNDARY AND REQUIRED PPE |  |  |  |  |  |  |  | ABB Electrical Safety Calculator V1.6a Jan. 2024 |
|  | Arc Flash boundary: |  | 0.1 m |  |  | Glove Class/ CAT: | Class 1 ≥7.5kV + CAT 3 Leather |  |  |
|  | Required PPE: |  | Multi-layer mandatory ATPV ≥8 Cal/cm2 and ATPV ≥25 Cal/cm2 + Ear Prot. + CAT 3 Complete Hood |  |  | Footwear: | Electrical Hazard Footwear “EH” |  |  |
|  | SHOCK HAZARD PROTECTION BOUNDARIES |  |  |  |  |  |  |  |  |
|  | Shock Hazard: |  | 122 VAC |  |  |  |  |  |  |
|  | Limited Approach: |  | 1m |  |  | Restricted Approach: | 0.3 m |  |  |
|  | Bus/Equipment ID: |  | SE PACHACAMAC 10 KV |  |  | Assessment Date: | 2026/01/09 |  |  |
|  | Protective Device (Upstream): |  |  | SALA TR2 |  |  |  |  |  |
|  | THIS LABEL IS FOR TEMPORARY USE AND MUST BE REMOVED AFTER SERVICE IS COMPLETED |  |  |  |  |  |  |  |  |
|  | IMPORTANT: This label was generated using estimated values ​​and may be used in the absence of a formal arc flash risk assessment. |  |  |  |  |  |  |  |  |